SPEC NOTE: This Guide Specification includes materials and methods for the application of 790-11 Hot Applied Rubberized Asphalt Waterproofing System.  Typical applications will include vertical applications on below grade tunnels, foundations and plaza decks preventing the penetration of water under hydrostatic pressure. This specification is ideally suited for premium performance waterproofing systems typical of Hospitals, Schools and commercial projects.  Although edited, this specification should be adapted to suit the requirements of individual projects.  It is prepared in CSI three part format and should be included as a separate section under Division 7 - Thermal and Moisture Protection.

# PART 1: GENERAL

1.01	GENERAL REQUIREMENTS

A.	The General Conditions, the Supplementary Conditions, the Instructions to Bidders and Division One General Requirements shall be read in conjunction with and govern this section.

B.	The Specification shall be read as a whole by all parties concerned.  Each Section may contain more or less than the complete work of any trade.  The Contractor is solely responsible to make clear to the Subcontractors the extent of their work.

1.02	DESCRIPTIONS

A.	Supply labour, materials, plant, tools and equipment to complete the Work as shown on the Drawings Architectural Division as specified herein including, but not limited to the following:

1.	Concrete Roof Deck (by others),

2.	Primer & 2 ply Hot Applied Rubberized Asphalt Waterproofing Membrane,

3.	Drainage Board,

4.	Back Fill (by others).

1.03	RELATED WORK

A.		Concrete:						Section [03 00 00]

B.	Rough Carpentry:		Section [06 00 00]

C.	Metal Flashing and Trim:	Section [07 00 00]

D.	Sealants:			Section [09 00 00]

1.04	REFERENCES

A.	The following standards are applicable to this section:

1.	ASTM D41: Asphalt Primer used in Roofing, Dampproofing, and Waterproofing.

2.	ASTM D92: Standard Test Method for Flash and Fire Points by Cleveland Open Cup.

3.	ASTM D1191: Standard Test Method for Concrete Joint Sealants.

4.	ASTM D3407: Standard Test Method for Joint Sealants, Hot Poured, for Concrete and Asphalt Pavements.

5.	ASTM E96: Water Vapor Transmission of Materials.

6.	CGSB 37-GP50M: Hot Applied, Rubberized Asphalt for Roofing and Waterproofing.

- UL Inc.: Class A Classification for use in Ballasted Systems.

1.05	SHOP DRAWINGS

A.		Submit shop drawings in accordance with Section [XXXXX] - [XXXXX].

1.06	DELIVERY, STORAGE AND HANDLING

A.		Delivery of Materials:

1.	Materials shall be delivered to the jobsite in undamaged and clearly marked containers indicating the name of manufacturer and product and shall have UL markings.

B.		Storage of Materials:

1.	Hot rubberized asphalt should be stored in closed containers outdoors.

2.	Store primer at temperatures of 40 degrees F and above to facilitate handling. Keep solvent away from open flame or excessive heat.

3.	Store roll materials on end.

C.	Handling of Materials:

1.	Primer contains solvent and is flammable. Do not use near open flame.

2.	Melting equipment shall consist of an indirect fired kettle with a double shell containing a high flash point heat transfer oil and mechanical agitator.

3.	Avoid overheating of hot rubberized asphalt. Recommended application temperature is 356 degrees F to 395 degrees F. Do not heat above 419 degrees F.

4.		Plant material shall be un-loaded from shipping containers as soon as possible.  All plants or pots shall be watered as they arrive on site.

5.		Pallets shall be shrink wrapped and secured prior to being lifted onto roof.

1.07	PROJECT/SITE CONDITIONS

- Environmental Requirements: No installation work shall be performed during rainy or inclement weather and on frost or wet covered surfaces.

B.	Protection:

1.	Temporary protection of the membrane shall be provided to prevent mechanical damage or damage from spillage of oil or solvents until such time as permanent protection is provided.

2.	Do not permit traffic of any kind over unprotected waterproof membranes. Apply protection board as soon as possible after installation of membrane.

C.	Ensure all preparation work is complete prior to installing waterproofing membrane.

1.08	SUBMITTLES

A.	Submit in writing, a document stating that the applicator of the primary membranes specified in this Section are recognized by the manufacturer as suitable for the execution of the Work.

B.	Prior to commencing the Work submit copies of manufacturers’ current ISO certification. Membrane, primers, sealants, adhesives and associated auxiliary materials shall be included.

C.	Prior to commencing the Work submit references clearly indicating that the membrane manufacturer has successfully completed projects on an annual basis of similar scope and nature for a minimum of fifteen years.  Submit references for a minimum of ten projects.

D.	Prior to commencing the Work submit manufacturers’ complete set of standard details for the air/vapour barrier and roofing membrane systems showing a continuous plane of air tightness throughout the building envelope.

1.09	QUALITY ASSURANCE

A.	Installer:

1.	Submit in writing a document stating that the applicator of the primary waterproofing membranes specified in this section is recognized by the manufacturer as suitable for the execution of the work.

2.		Prior to commencing the work, submit copies of manufacturers’ current ISO certification.  Membrane, primers, sealants, and adhesives shall be manufactured in an ISO registered facility.

3.	Perform work in accordance with the printed requirements of the waterproofing membrane manufacturer and this specification.

4.	Maintain one copy of manufacturer's instructions on site.

5.	At the beginning of the work and at all times during the execution of the work, allow access to work site by the waterproofing membrane manufacturer's representative.

6.	Pre-Installation Conference: Convene prior to commencing work of this section.

7.	Mock-Up: Where directed, construct typical assembly incorporating substrate, primer and waterproofing membrane. Allow 24 hours for inspection of mock-up before proceeding. Mock-up may remain as part of the work.

B.	All components used in this section shall be produced by one manufacturer, including primary membrane, liquid sealants, primers, mastics, and adhesives. Primary membrane shall meet CGSB 37-GP-50-M89.

C.	The rubberized asphalt membrane product shall contain an inert clay filler to enable the product to be resistant to acids (fertilizers, building washes and acid rain).

1.10	MEMBRANE MANUFACTURER QUALIFICATIONS

A.		Manufacturer shall demonstrate qualifications to supply materials of this section by certifying the following:

1.	Membrane Manufacturer must show evidence that the specified rubberized asphalt has been manufactured by the same source for fifteen (15) years and successfully installed on a yearly basis for a minimum of fifteen (15) years on projects of similar scope and complexity.

- Membrane Manufacturer must not issue warranties for terms longer than they have been manufacturing their hot fluid rubberized asphalt membrane.

1.11	PRECONSTRUCTION CONFERENCE

A.	The manufacturers of the waterproofing/roofing membrane will meet with the necessary parties at the jobsite to review and discuss project conditions as it relates to the integrity of the waterproofing assembly.

1.12	ALTERNATES

A. 	Submit requests for alternates in accordance with Section [XXXXX] - [XXXXX].

B.	Alternate submission format to include:

1.	Submit evidence that alternate materials meet or exceed performance characteristics of Product requirements and documentation from an approved independent testing laboratory certifying that the performance of the waterproofing membrane system including drain boards and transition sheets, exceed the requirements of the local Building Code.

2.	Submit copies of manufacturers’ current ISO certification.

3.	Submit references clearly indicating that the membrane manufacturer has successfully completed projects on a annual basis of similar scope and nature for a minimum of fifteen years.

4.		Submit manufacturers’ complete set of standard details for the roofing membrane systems showing a continuous plane of water tightness throughout the building envelope.

C.	Submit requests for alternates to this specification a minimum of fifteen (10) working days prior to tender closing for evaluation. Include a list of 25 projects executed over the past fifteen years.

D.	Acceptable alternates will be confirmed by addendum. Substitute materials not approved in writing prior to tender closing shall not be permitted for use on this project.

1.13	WATERPROOFING MEMBRANE WARRANTY

SPEC NOTE: There are three warranty configurations available from Henry. Choose 1.13.A, 1.13.B or 1.13.C from the following. Note that charges apply to certain warranties and scope of coverage varies. Contact Henry for complete details.

A.	Manufacturer's Material Warranty:

1.	Contractor hereby warrants that the waterproofing membrane and membrane flashings for leak coverage, but for two years.

2.	Waterproofing membrane manufacturer hereby warrants that the membrane and membrane flashings for leak coverage as a result of faulty materials for a period of 10 years from the date of substantial completion.

B.	Manufacturer's System Warranty:

1.	Contractor hereby warrants that the waterproofing membrane and membrane flashings for leak coveragef, but for two years.

2.	Waterproofing membrane manufacturer hereby warrants that the membrane and membrane flashings will remain in a watertight condition for leak coverage for a period of [5 years] [10 years] [15 years] from the date of substantial completion.

C.	Manufacturer's Single Source Watertight Warranty:

1.	Contractor hereby warrants that the waterproofing membrane and membrane flashings for leak coverage, but for two years.

2.	Waterproofing membrane manufacturer hereby warrants that the membrane and membrane flashings for leak coverage for a period of [5 years] [10 years] [15 years] from the date of substantial completion.

## PART 2: MATERIALS

2.01	MANUFACTURER

A.	Components and membrane materials must be obtained as a single-source from the membrane manufacturer to ensure total system compatibility and integrity.

      - Acceptable Manufacturer: 	Henry Company.

909 N Sepulveda Blvd, Suite 650

El Segundo, CA  90245

(800) 598-7663

Web Site: www.Henry.com

2.        Acceptable Distributor:		Bowman Construction Supply

10801 E. 54th Avenue

Denver, CO 80239

Phone: (303) 696-8960

www.bowmanconstructionsupply.com

2.02	PRIMARY WATEPROOFING MEMBRANE (Basis-of-Design Product)

A.	Primary waterproofing membrane shall be 790-11 manufactured by Henry, an SBS modified hot applied rubberized asphalt composed of a specially selected blend of refined asphalts, synthetic rubber and mineral stabilizers, and having the following physical properties:

1.	Solids Content: 100%;

2.	Low Temperature Flexibility and Adhesion: No cracking, delamination or loss of adhesion @ 13 degrees F in accordance with CGSB 37-GP-50-M89;

3.	Flow (1/8 inch film on 75% angle for 5 hours @ 140 degrees F): No flow in accordance with ASTM D1191;

4.	Cone Penetration: More than 10 @ 32 degrees F, less than 110 @ 77 degrees F, less than 200 @ 122 degrees F in accordance with ASTM D1191;

5.	Water Absorption: Gain of 0.09g in accordance with CGSB 37-GP-50-M89;

6.	Flash Point (Open Cup): 545 degrees F in accordance with ASTM D92;

7.	Water Vapor Permeance (3mm Film): 0.01 perms in accordance with ASTM E96 Procedure A and 0.02 perms in accordance with ASTM E96 Procedure E.

8.	Ratio of Toughness to Peak Load: 0.04 min. in accordance with CGSB 37-GP-50-M89.

9.	Toughness: 9.2J in accordance with CGSB 37-GP-50-M89.

10.	Crack Bridging Capability: No cracking, splitting or loss of adhesion in accordance with CGSB 37-GP-50-M89.

11.	Heat Stability (5 hours @ 390 degrees F): Meets flow, penetration and low temperature flexibility in accordance with CGSB 37-GP-50-M89.

SPEC NOTE: Henry manufacturers two types of primers for the 790-11 waterproofing system. 910-01 is a standard asphaltic primer while 930-18 is a polymer modified primer. Significantly improved adhesion can be achieved using 930-18. Choose from the following.

B.	Primers

1.	Asphalt Primer:

a.	Asphalt primer conforming to ASTM D41 shall be Henry #103 or Henry#104 Asphalt Penetrating Primer manufactured by Henry.

2.	Polymer Modified Primer:

a.	Synthetic rubber based type primer shall be 930-18 Primer for Polymer Modified Membranes manufactured by Henry, being fully compatible with the primary waterproofing membrane and membrane flashings.

SPEC NOTE: There are options for exposed flashing membranes. Henry recommends the use of SBS modified bitumen flashing membranes in place of standard neoprene sheets. For exposed flashings choose either 2.02.C.1. or 2.02.C.2.

C.	Cap Flashing Membranes:

1.	Granulated cap flashings membrane shall be modifiedPLUS NP180gM4 manufactured by Henry, an SBS modified bitumen membrane having a polyethylene lower surface and a ceramic granule top surface, reinforced with a non-woven polyester reinforcement, designed specifically for hot mop applications, and having the following physical properties in accordance with ASTM D5147:

a.	Thickness: 0.140 inches 140 mils;

b.	Tensile strength @ 0 degrees F: 113 lbf/inch (md), 100 lbf/inch (xd);

c.	Elongation @ 0 degrrees F: 40% (md & xd);

d.	Low temperature flexibility: -15 degrees F;

2.	Exposed flashings and expansion joint membrane shall be Neoflash and Neoflash Adhesive manufactured by Henry. Neoprene type, uncured and having a min. thickness of 60mils.

SPEC NOTE: For concealed flashing, crack treatment, reinforcement & slip sheet membranes, SBS modified bitumen membranes may be either applied in 790-11 or self-adhered. The specifier may allow the contractor to choose or may select modifiedPLUSNP180s/s for applications set in 790-11, modifiedPLUS G100 Tack Sheet for self-adhered applications and Blueskin WP200 for waterproofing transition membranes.

D. 	Concealed Flashing, Crack Treatment, Reinforcement & Slip Sheet Membranes:

1.	Mop grade membrane shall be modifiedPLUS NP180s/s manufactured by Henry, an SBS modified bitumen membrane having a minimum thickness of 90 mils and a non-woven polyester reinforcement of 180 g/m2 meeting CGSB-37-GP-56M Type 2 Class C Grade 2.  The upper and lower surface shall be sanded and be fully compatible with the primary membrane.

2.		Self-Adhering crack treatment membrane shall be modifiedPLUSG100 Tack Sheet manufactured by Henry, an SBS modified bitumen membrane having a minimum thickness of 80 mils and a fibre glass reinforcement of 100 g/m2 meeting CGSB-37-GP-56M Type 2 Class C Grade 1.  The upper surface shall be sanded and be fully compatible with the primary membrane, the lower surface shall be self-adhering with silicone treated release paper.

3.	Self-Adhering waterproofing transition membrane for vertical walls shall be Blueskin WP 200 manufactured by Henry, a 60 mils min. thick SBS modified bitumen, self-adhering sheet membrane with a cross-laminated polyethylene film, and having a tensile film strength of 34.5 MPa to ASTM D882 and Elongation of 300% to ASTM D412.

E.	Fabric Reinforcement:

1.	Polyester Fabric reinforcement sheet as supplied by Henry, an inorganic spun bonded polyester fabric sheet with sufficient porosity to allow good interply bonding between layers of waterproofing membrane.

F.		Termination Sealant:

1.	Termination sealant shall be POLYBITUME 570-05 Polymer Modified Sealing Compound manufactured by Henry, compatible with sheet waterproofing membrane, substrate and insulation materials, complies with CGSB 37.29, remains flexible with ageing and chemically resistant to alkalis, calcium chloride, mild acid and salt solutions.

- Securement Bars:

1.	Securement bars shall be continuous aluminium, stainless steel or galvanized metal, 1/8 inch x 1 inch in size and shall be pre-drilled for non-corrosive screw attachment on a maximum of 8 inch centers.

2.03	PREFABRICATED DRAIN BOARDS: Two part prefabricated geocomposite drain board consisting of a formed polystyrene or PVC core covered on one side with a woven or non-woven polypropylene filter fabric:

A.	Henry DB 200: For vertical and horizontal installations, shallower depths.

B.	Henry DB 500: For vertical installations requiring high compressive strength and high flow capacity.

2. 04	PREFABRICATED DRAIN BOARD ACCESSORIES

A.	Securement Bars: Continuous 1/4 inch x 3/4 inch HDPE bar for screw attachment.

B.	Moulding Strip:  Continuous 3 ½ inch wide ‘Z’ flashing strip to fit over exposed top edge of drain board.

C.	Drain Board Plugs & Nails:  HDPE pre-moulded washer to fit dimples c/w high strength, corrosion resistant concrete nails, UCAN AFH 37 or equal.

## PART 3: EXECUTION

3.01	EXAMINATION

A.	Acceptable substrates are cast-in-place and precast concrete and plywood. Metal pan decks to which concrete is poured must be venting type. Lightweight concrete is not an acceptable substrate.

B.	Verify that surfaces and conditions are ready to accept the work of this section. Commencement of the work or any parts thereof shall mean acceptance of the substrate.

3.02	PREPARATION

A.	All surfaces must be sound, dry, clean and free of oil, grease, dirt, excess mortar, frost or other contaminants. Fill spalled areas in substrate to provide an even plane and remove scaling or laitant concrete. Remove curing compounds or any foreign matter detrimental to the adhesion of the primary waterproofing membrane or membrane flashings.

B.	New concrete should be cured for a minimum of fourteen days and must be dry before waterproofing membranes are applied. Concrete in vented metal pan decks must be cured a minimum of sixty days.

C.	Concrete shall have a wood float finish. Steel float finishes are too smooth and compromise the adhesion of the waterproofing system. Decks with a steel float finish must be sandblasted or equivalent prior to the application of the waterproofing system.

D.	Prefabricated expansion joint assemblies should be in place prior to the application of the primary waterproofing assembly.

3.03	 INSTALLATION OF WATERPROOFING MEMBRANE

A.	Primer:

1.	Apply primer as recommended by manufacturer and allow to dry prior to the application of the primary waterproofing membrane or membrane flashings.

B.	Joint Treatment For Precast Concrete Deck:

1.	Reinforce joints along length of units with a strip of 12 inch wide Polyester Fabric set in an 18 inch wide, 1/8 inch thick coat of membrane.

2.	At joints occurring along the width of the precast units, reinforce with a minimum 12 inch wide crack treatment sheet embedded into an 18 inch wide, 1/8 inch thick coat of membrane.

C.	Deck to Vertical Junctures:

1.	Apply hot rubberized asphalt membrane to provide a thickness of approximately 1/8 inch to the vertical faces and a minimum of 4 inches out onto the horizontal surface.

2.	Embed flashing sheet in the hot rubberized asphalt membrane, avoiding any wrinkles or fishmouths, extending a minimum of 3 inches out onto the horizontal surface.

3.	Mechanically attach the flashing sheet to vertical surfaces with metal securement bar where height of flashing exceeds 12 inches. Lap flashing sheet minimum 3 inches on ends.

4.	At monolithic pour, use fabric reinforcement as option to flashing sheet.

D.	Expansion Joints (Neoprene):

- Expansion joint membrane can be applied in a bed of primary waterproofing membrane or adhered to substrate with expansion joint adhesive. Place expansion joint membrane into expansion joint adhesive as recommended by manufacturers’ written instructions.

- Loop expansion joint membrane down into expansion joint, embedded into a 1/8 inch thick layer of hot rubberized asphalt membrane. Ensure that the depth of loop is a minimum 1-1/2 inch.

- Extend expansion joint membrane minimum of 3 inches on each side of joint. Seal end joints a minimum of 6 inches and seal with a 1/8 inch coat of membrane. Fill loop with membrane as required.

- Secure top of expansion joint membrane with continuous fixing bar at vertical wall locations.

E.	Crack Treatment:

1.	Seal cracks and joints 1/16 inch to 1/8 inch in width with a 12 inch wide, 1/8 inch thick coat of hot rubberized asphalt membrane and a 6 inch wide strip of fabric reinforcement, centered over joint.

2.	Seal cracks and joints 1/8 inch to 1/4 inch in width with a 12 inch wide, 1/8 inch thick coat of hot rubberized asphalt membrane and a 6 inch wide strip of crack treatment or expansion joint membrane, centered over joint.

F.	Membrane Flashing At Drains:

1.	Coat areas around the drains with hot rubberized asphalt membrane at a thickness of 1/8 inch.

- Place flashing sheet over the coated drain flange and extending a minimum 6 inches around the flange.

3.	Apply a second coat of hot rubberized asphalt membrane over the flashing sheet at a thickness of 1/8 inch.

4.	Apply clamping ring exerting sufficient pressure to affect a seal between clamping

ring and membrane. Temporarily block all drains during the application of ballast, or other materials that might block the drains. Remove blocking when work is not in progress and upon completion.

G.	Membrane Flashing At Protrusions:

1.	At mechanical vent, protrusions and pipe penetrations provide flashing sheet set into 1/8 inch layer of hot rubberized asphalt membrane. Overcoat and seal with membrane. Install clamps as required.

2.	At pitch pockets, place pan on top of a 1/8 inch layer of membrane and attach into roof deck. Set flashing sheet into 1/8 inch hot rubberized asphalt membrane over top of flange. Fill pitch pocket with rubberized asphalt or rubber asphalt sealer in order to shed water.

H.		Membrane Flashing At Vertical Junctures (Self-Adhering Membrane):

1.	Apply self-adhering waterproofing membrane to prepared substrate in lengths of 6 feet or less.

2.	Horizontal to vertical inside corner transition areas are to be pre-treated with a fillet bead of termination sealant extending ¾ inch vertically and horizontally from the corner. Apply a minimum 10 inch wide strip of waterproofing membrane centred at the joint.

3.	All outside corners are to be pre-treated with a minimum 10 inch strip of waterproofing membrane centred at the joint.

4.	Where three or more planes come into contact reinforce with cut sections of waterproofing membrane reinforcing sheet as per manufacturer’s instructions.

5.	Provide 2-1/2 inch laps at both sides and ends.  Position for alignment and remove protective film. Press firmly into place. Promptly roll all laps with a counter top roller to effect seal. If more than one length is required on a vertical surface, apply in a shingle fashion.

6.	Terminate membrane using termination sealant and counter flashing as indicated.

7.	All laps within 12 inches of a 90 degree change in plane are to be sealed with termination sealant.

I.	Application of Hot Rubberized Asphalt Membrane:

1.		Ensure deck is ready to receive hot applied rubberized asphalt membrane.  Where torch applied flashing membranes have been used, ensure top polyfilm has been scorched away prior to application of the membrane.

2.		Apply membrane smooth, free from air pockets, wrinkles, or tears and to manufacturer's Instructions.  Ensure full bond of membrane to substrate.

3.		Apply first layer of hot rubberized asphalt membrane evenly to a minimum thickness of 90 mils to form a continuous monolithic coating over horizontal and vertical surfaces including previously reinforced areas.

4.		Apply fabric reinforcing sheet and firmly press into first layer of hot membrane.  Overlap fabric approximately ¼ inch ensuring that a layer of membrane is present between overlaps.  Apply second layer of membrane over the fabric to a minimum thickness of 1/8 inches (125 mils) providing a total thickness of 215 mils.

J.		Installation of Protection Course/Separation Sheet

1.		Protection course shall be rolled onto hot applied rubberized asphalt membrane while still warm and tacky.

2.		Lap protection course 2 inches on side laps and 6 inches on end laps.

3.		Starting at the low points or drains lay the protection course membrane in full continuous sheets in a shingle pattern. Stager all end laps.

3.04	Installation of Drainage Board (Vertical)

- Align and hang drainage up to foundation wall. Position bottom edge of drainage board to be in moderate contact with weeping tile system.

- Secure drainage board to foundation wall with nails and washers spaced 450 mm o/c horizontally. Install minimum of 2 rows staggered and spaced 150 mm apart and min 150 from top edge.

- Align and install termination strip along top edge with nails spaced 300 mm o/c and seal with termination sealant.

- Align and install moulding strip over completed top edge detail.

- Overlap end laps, pull back loose fabric to expose drain core and position core of second panel over the overlap flange of first panel.

- Bend drain board to create inside corners and cut board to create outside corners, provide 75 mm of extra fabric to wrap corner.

- Stagger or offset joints of drain board sheets.

- Place all subsequent sheets in an overlapping single fashion.

- Backfill bottom edge in conjunction with weeping tile system.

3.05	INSTALLATION OF BACKFILL: See Division 2 Site Works

3.06	FIELD QUALITY CONTROL

A.	Final Inspection and Approval:

- Final inspection of completed work shall be carried out by the owner's representative, the contractor and Henry.

3.07	CLEAN-UP

A.	Promptly as the work proceeds and on completion, clean up and remove from the premises 			all rubbish and surplus materials resulting from the foregoing work.

- Clean to the consultant's approval, soiled surfaces, spatters, and damage caused by work of

this Section.

- Check area drains to ensure cleanliness and proper function, and remove debris, equipment and excess material from the site.

END OF SECTION